## Integration Checklist
MBCx Project Name
MBCx Project Number
Software Tool Name
|  |  | General Clarifications |  | Service Provider Notes | RESOURCE INNOVATIONS USE ONLY
|  | Integration Documentation Item | Required Info | Example(s) |  | Date Submitted | Saved to "Integration" Folder on Network? | Confirmed Complete | Notes: Project Specific
Proof of Integration | 1 | Email confirmation from Service Provider and file Submission Through Europa | Confirming full integration Scope of Work is completed | - |  |  | No | Yes
| 2 | List of monitored equipment • Typically Excel file | List all equipment names/IDs including terminal equipment, if name is encoded please include descriptive name. Not required- Equipment schedule, size, rating, etc. | AHU-1, AHU-2, CH-1, FPB-1, etc. |  |  | No | No
| 3 | Points List • Names of all monitored points • Typically Excel file | Point tag, name, unit (understandable) Needs to be comprehensive | E_1801_AHU01_CHWR_TMP Chilled Water Supply Temp °F |  |  | No | No
| 4 | Sample Trend Data File • Pulled remotely from BAS • XLS or CSV format | At least 1 AHU, 1 terminal box, and chiller plant- show all points for 1 week with 15 minute intervals. | - |  |  | No | No
| 5 | List of Top 10 Algorithms • From MBCx analytics to identify Energy Conservation Measures (ECMs) at the building | Logic rules showing how exceptions will be identified. | If OAT< 50 and Chiller Status = 1; If Occ = 0 AND OAdamper > 0 |  |  | No | No
| 6 | Sample Exception/Error Report •Indicate areas to investigate for savings (PDF or Excel file) | Show algorithms have been run and exceptions flagged for further investigation. | - |  |  | No | No
| 7 | Customer Web Portal • Read only access/login (preferred) and a demo of portal | 1. Provide login credentials to Resource Innovations and a demo, enough to confirm portal is ready. 2. Alternate option for service providers that have completed 3 MBCx Integrations- see description in Example(s) | If alternate option applies provide the following screenshots in place of a demo: • Main screen- 1 • Exception Report- 1 • AHU trends- a sampling per Group B guidelines in the M&V guidelines • Boiler/hot water pump trends- all • Chiller Plant/ chilled water pumps/cooling tower fans/pumps trends- all • VAV/FPB trends- 8 – 10 |  |  | No | No
VALIDATION
Yes
No
N/A