## ASHC
Door Heater Controls for Cooler or Freezer
Source | IL TRM 4.6.3 Page 795
Link | https://www.ilsag.info/wp-content/uploads/IL-TRM_Effective_010125_v13.0_Vol_2_C_and_I_09202024_FINAL.pdf
Instructions
Please populate the fields in orange with the appropriate data.
Category | Input | Case Type |  | Control Type |  | Case Temperature Range |  | Annual Hours | Summer Coincident Factor
Case Type | Cooler | kWbase |  | ESF |  | Bonus Factor |  | 8766 | 0
Number of Doors | 1 | Freezer | 0.23 | Humidity Based Control | 45% | Low (-35F - 0F) | 1.5
Control Type | Humidity Based Control | Cooler | 0.066 | Conductivity Based Control | 45% | Medium (0F - 20F) | 1.3
Case Temperature Range | Low (-35F - 0F) |  |  |  |  | High (20F - 45F) | 1.3
ΔkWH | 391
ΔkW | 0
ΔTherms | 0

## EC Motor
EC Motors for Walk-in and Reach-in Coolers/Freezers
Source | IL TRM 4.6.4 Page 798
Link | https://www.ilsag.info/wp-content/uploads/IL-TRM_Effective_010125_v13.0_Vol_2_C_and_I_09202024_FINAL.pdf
Instructions
Please populate the fields in orange with the appropriate data.
Category | Input | Savings Per Motor |  |  | Annual Hours | Coincidence Factor
Evaporator Fan Motor Rating | 1/5 HP | Evaporator Fan Motor Rating (ECM) | Annual kWh Savings per Motor | Peak kW Savings per Motor | 8760 | 1
Number of Motors | 1 | 16 W | 652 | 0.074
|  | 1/15 - 1/20 HP | 1586 | 0.181
ΔkWH | 2320 | 1/5 HP | 2320 | 0.265
ΔkW | 0.3 | 1/3 HP | 3380 | 0.386
ΔTherms | 0 | 1/2 HP | 4481 | 0.512
|  | 3/4 HP | 5293 | 0.604
If ECM HP is unknown, use 1/15 HP, therefore 1,586 kWh saved/motor

## Evaporator Fan Control
Evaporator Fan Control for EC Motors
Source | IL TRM4.6.6 Page 804
Link | https://www.ilsag.info/wp-content/uploads/IL-TRM_Effective_010125_v13.0_Vol_2_C_and_I_09202024_FINAL.pdf
Instructions
Please populate the fields in orange with the appropriate data.
Category | Input | Savings Per Motor
Evaporator Fan Motor Rating (ECM) | 1/5 HP | Evaporator Fan Motor Rating (ECM) | Annual kWh Savings per Motor | Peak kW Savings per Motor
Number of Motors | 1 | 16 W | 198 | 0.023
|  | 1/15 - 1/20 HP | 293 | 0.033
ΔkWH | 856 | 1/5 HP | 856 | 0.098
ΔkW | 0.1 | 1/3 HP | 1419 | 0.162
ΔTherms | 0 | 1/2 HP | 2126 | 0.243
|  | 3/4 HP | 3209 | 0.366

## Floating Head Pressure Control
Floating Head Pressure Control
Source | IL TRM 4.6.14 Page 834
Link | https://www.ilsag.info/wp-content/uploads/IL-TRM_Effective_010125_v13.0_Vol_2_C_and_I_09202024_FINAL.pdf
Instructions
Please populate the fields in orange with the appropriate data.
Category | Input | Average Annual Savings (kWh/hp) | Zone | Unit Type | Low Temperature (Freezer) | Medium Temperature (Refrigerator) | Unknown Temperature | Concat
Compressor hp | 10 | 301 | Springfield | Self-Contained Unit | 252 | 131 | 170 | SpringfieldSelf-Contained Unit
Weather Zone | Belleville |  |  | Remote Condensing Unit | 403 | 377 | 385 | SpringfieldRemote Condensing Unit
Condensing Unit Type | Remote Condensing Unit |  |  | Unknown | 327 | 254 | 278 | SpringfieldUnknown
Temperature Range | Medium Temperature (Refrigerator) |  | Belleville | Self-Contained Unit | 252 | 131 | 170 | BellevilleSelf-Contained Unit
|  |  |  | Remote Condensing Unit | 321 | 301 | 307 | BellevilleRemote Condensing Unit
ΔkWH | 3010 |  |  | Unknown | 287 | 216 | 239 | BellevilleUnknown
ΔkW | 0 |  | Marion | Self-Contained Unit | 252 | 131 | 170 | MarionSelf-Contained Unit
ΔTherms | 0 |  |  | Remote Condensing Unit | 328 | 307 | 314 | MarionRemote Condensing Unit
|  |  |  | Unknown | 290 | 219 | 242 | MarionUnknown
|  |  | Chicago | Self-Contained Unit | 252 | 131 | 170 | ChicagoSelf-Contained Unit
|  |  |  | Remote Condensing Unit | 465 | 435 | 445 | ChicagoRemote Condensing Unit
|  |  |  | Unknown | 358 | 283 | 307 | ChicagoUnknown
|  |  | Rockford | Self-Contained Unit | 252 | 131 | 170 | RockfordSelf-Contained Unit
|  |  |  | Remote Condensing Unit | 482 | 451 | 461 | RockfordRemote Condensing Unit
|  |  |  | Unknown | 367 | 291 | 315 | RockfordUnknown

## Q-sync Motors
Q-Sync Motors for Walk-in and Reach-in Coolers/Freezers
| Source | IL TRM 4.6.11 Page 820
| Link | https://www.ilsag.info/wp-content/uploads/IL-TRM_Effective_010125_v13.0_Vol_2_C_and_I_09202024_FINAL.pdf
Instructions
Please populate the fields in orange with the appropriate data.
Enter number of SP and EC motors to be replaced for both medium-temp and low-temp applications Enter number of unknown type motors to be replaced Select the application for the unknown type motors If unknown existing motor type is for walk-in cooler/freezer please enter motor as PSC
| Category | Input |  | Savings Per Motor
| # of Shaded Pole (SP) motors replaced (Med-Temp, 9-12W) | 1 |  | Evaporator Fan Motor Rating (of Q-Sync motor) | Baseline | Annual kWh Savings/motor | kW Savings/motor
| # of Shaded Pole (SP) motors replaced (Low-Temp, 9-12W) | 1
| # of Electronically Commutated (EC) motors replaced (Med-Temp) | 1 |  | 9-12W | shaded-pole motor, med-temp | 412.07 | 0.047
| # of Electronically Commutated (EC) motors replaced (Low-Temp) | 1 |  | 9-12W | shaded-pole motor, low-temp | 509.929 | 0.059
| # of Shaded Pole (SP) motors replaced (Med-Temp, 38-50W) | 1 |  | 9-12W | EC motor, med-temp | 76.036 | 0.009
| # of Shaded Pole (SP) motors replaced (Low-Temp, 38-50W) | 1 |  | 9-12W | EC ,motor, low-temp | 94.094 | 0.011
| # of Permanent Split Capacitor (PSC) motors replaced (Med-Temp) | 1 |  | 38-50W | shaded-pole motor, med-temp | 1020.364 | 0.116
| # of Permanent Split Capacitor (PSC) motors replaced (Low-Temp) | 1 |  | 38-50W | shaded-pole motor, low-temp | 1262.682 | 0.147
| # of unkown type motors replaced | 1 |  | 38-50W | PSC motor, med-temp | 295.562 | 0.034
| Unknown type application | Other Retail Categories |  | 38-50W | PSC motor, low-temp | 365.753 | 0.043
| Calculation Parameters |  |  | Application | WSPM | WECM | Wmed-temp* | Wlow-temp*
Average evaporator fan motor power in refrigerated display cases | Shaded-pole motor input (W) | 50 |  | Supermarkets | 0.6 | 0.4 | 0.68 | 0.32
| EC motor input (W) | 22.6 |  | Other Food Retail Formats | 0.8 | 0.2 | 0.68 | 0.32
| Q-Sync motor input (W) | 16.4 |  | Other Retail Categories | 0.7 | 0.3 | 0.68 | 0.32
Average evaporator fan motor power in walk-in coolers/freezers | Shaded-pole motor input (W) | 120.4 |  | Restaurants and Bars | 0.85 | 0.15 | 0.68 | 0.32
| PSC motor input (W) | 61.3 |  | Beverage Vending Machines | 0.85 | 0.15 | 0.68 | 0.32
| Q-Sync motor input (W) | 37.2
| Med-Temp Annual Hrs | 8760
| Low-Temp Annual Hrs | 8578
| Weighting of unknown motors that are SP | 0.7
| Weighting of unknown motors that are EC | 0.3
| Weighting of unknown motors that are Med Temp | 0.68
| Weighting of unknown motors that are Low Temp | 0.32
| Category - Refrigerated Display Cases | Annual Energy Savings (kWh) | kW Savings
| Shaded Pole (Med-Temp, 9-12W) | 412.07 | 0.047
| Shaded Pole (Low-Temp, 9-12W) | 509.929 | 0.059
| EC (Med-Temp) | 76.036 | 0.009
| EC (Low-Temp) | 94.094 | 0.011
| Unkown Type | 334.9138 | 0
| Total | 1427.0428 | 0.126
| Category - Walk-in Coolers and Freezers | Annual Energy Savings (kWh) | kW Savings
| Shaded Pole (Med-Temp, 38-50W) | 1020.364 | 0.116
| Shaded Pole (Low-Temp, 38-50W) | 1262.682 | 0.147
| PSC (Med-Temp) | 295.562 | 0.034
| PSC (Low-Temp) | 365.753 | 0.043
| Total | 2944.361 | 0.34

## Edition Updates
Updates
TRM Edition | https://www.ilsag.info/wp-content/uploads/IL-TRM_Effective_010125_v13.0_Vol_2_C_and_I_09202024_FINAL.pdf
Update Date | 2025-08-22
Calculators
ASHC | Summer coincident factor updated
Floating Head Pressure Control | Springfield Zone - Remote Condensing Unit - Values updated for medium and unknow temperatures
Q-sync Motors | Savings Per Motor - Annual kWh Savings/motor - Values Updated

## Programmable T-stat (hidden)
Programmable Thermostats
Source | IL TRM Page 231
Link | http://ilsagfiles.org/SAG_files/Technical_Reference_Manual/Version_7/Final_9-28-18/IL-TRM_Effective_010119_v7.0_Vol_2_C_and_I_092818_Final.pdf
Instructions
Please populate the fields in orange with the appropriate data.
Enter: Cooling capacity in tons (Typical RTU: 5 tons) Heating capacity in kBtuh (Typical RTU: 115 kBtuh) Select: Building Type Fan Mode During Occupied Periods Fan Mode During Unoccupied Periods Climate Zone Enter degrees of cooling set back (values must be between 0-15 Fahrenheit) Enter degrees of heating set back (values must be between 0-15 Fahrenheit) | [10 empty] | Fu | Fuu
[11 empty] | 1 | 1
Baseline
Category | Input | [9 empty] | Baseline | Upgrade
Tons Cooling Capacity | 10 | Electric Energy Use Climate Zone Coefficients and Minimum Weekly Hours Occupied | [7 empty] | EQUATIONS (ELECTRIC) | kWh/ton | kWh/ton
kBtuh Heating Capacity | 230 | Building Type and Fan Mode During Occupied Period |  | Climate Zone Coefficient (CZ)433 |  |  |  |  | Minimum Ws
Building Type | Office - Low Rise |  |  | 1 | 2 | 3 | 4 | 5
Fan Mode During Occupied Periods | Continuous | Assembly Continuous |  | 911.366 | 928.924 | 1152.83 | 1208.999 | 1210.173 | 98 | CZ+Fu*(0.83*Tc+0.83*Th+1.67*Ws-293.018)-0.0922*Tc*Th+1.291*Ws | 4909.429 | 4917.177
Fan Mode During Unoccupied Periods | Intermittent | Assembly Intermittent |  | 735.752 | 762.831 | 966.562 | 998.927 | 1028.906 |  | CZ+Fu*(1.911-0.12*Tc)+Tc*(0.00311*Ws-0.229)+0.11*Ws | 5047.553 | 5046.4853
Energy Type | Electric Energy | Convenience Store Continuous |  | 4817.094 | 4832.784 | 5139.133 | 5182.161 | 5208.608 | 108 | CZ+Fu*(-28.629*Tc-11.69*Th+19.118*Ws-2935.12)+0.909*Ws | 3205.957 | 2917.283
Climate Zone | 2 | Convenience Store Intermittent |  | 1478.133 | 1514.568 | 1784.384 | 1843.463 | 1930.47 |  | CZ+Tc*(0.0863*Ws-12.688)+Th*(0.043*Ws-6.38)+1.669*Ws CZ+Tc*(0.0863*Ws-12.688)+Th*(0.043*Ws-6.38)+1.669*Ws CZ+Tc*(0.0863*Ws-12.688)+Th*(0.043*Ws-6.38)+1.669*WsCZ+Tc*(0.0863*Ws-12.688)+Th*(0.043*Ws-6.38)+1.669*Ws CZ+Tc*(0.0863*Ws-12.688)+Th*(0.043*Ws-6.38)+1.669*Ws | 5131.387 | 5043.588
Degrees of Cooling Setback | 0 | Office - Low Rise Continuous |  | 5047.662 | 5039.592 | 5187.924 | 5217.672 | 5177.449 | 55 | CZ+Fu*(7.082*Tc-41.199*Th+18.734*Ws-3288.55)+Tc*(0.205*Ws-34.929) | 2781.412 | 2269.99
Degrees of Heating Setback | 0 | Office - Low Rise Intermittent |  | 825.072 | 808.965 | 946.571 | 979.421 | 945.418 |  | CZ+Tc*(0.0806*Ws-8.984)+Th*(0.0864*Ws-9.558)+1.178*Ws | 5104.382 | 5029.016
|  | Religious Facility Continuous |  | 4197.117 | 4172.858 | 4380.025 | 4370.008 | 4356.054 | 133 | CZ+Fu*(-1.579*Tc-18.14*Th+15.01*Ws-2417.74)+Tc*(0.177*Ws-26.412) | 3447.402 | 3156.466
Calculation Parameters |  | Religious Facility Intermittent |  | 632.404 | 603.395 | 678.294 | 664.717 | 616.853 |  | CZ+Fu*(0.266*Tc-2.067)+Tc*(0.0295*Ws-4.502)+Th*(0.0517*Ws-8.251)+0.735*Ws | 5077.95 | 5008.194
Climate Zone Coefficient | 5039.592 | Restaurant - Fast Food Continuous |  | 1342.988 | 1378.661 | 1664.018 | 1714.201 | 1727.841 | 108 | CZ+Fu*(0.678*Tc+0.257*Th+2.88*Ws-494.006)+Tc*(0.0231*Ws*4.074)+Th*(0.00936*Ws-1.655)+0.918*Ws | 4754.476 | 4780.7681
Weekly Hours | 55 | Restaurant - Fast Food Intermittent |  | 993.764 | 1039.643 | 1307.8 | 1340.544 | 1389.791 |  | CZ+Fu*(0.377*Tc+0.124*Th+0.13*Ws-24.893)+Tc*(-0.0143*Th+0.0166*Ws-2.691)+0.898*Ws | 5071.239 | 5063.215
|  | Restaurant - Full Service Continuous |  | 4070.35 | 4094.742 | 4428.966 | 4501.829 | 4522.522 | 117 | CZ+Fu*(-8.41*Th+11.766*Ws-1910.81)+Tc*(0.282*Ws-43.851) | 3775.912 | 3521.766
Baseline |  | Restaurant - Full Service Intermittent |  | 1472.014 | 1516.05 | 1856.108 | 1938.441 | 2056.45 |  | CZ+0.123*Fu*Tc+Tc*(0.0561*Ws-8.237)+Th*(0.0219*Ws-3.284)+1.038*Ws | 5096.682 | 5045.716
kWH | 27814.12 | Retail - Department Store Continuous |  | 1510.201 | 1496.47 | 1706.105 | 1716.128 | 1688.464 | 93 | CZ+Fu*(-1.475*Th+0.755*Ws-114.373)+Th*(0.151*Ws-24.016)+1.612*Ws | 5055.404 | 4883.544
|  | Retail - Department Store Intermittent |  | 701.27 | 702.129 | 847.735 | 875.12 | 881.677 |  | CZ+Tc*(0.0173*Ws-1.912)+Th*(0.0249*Ws-3.29)+0.511*Ws | 5067.697 | 5042.729
Upgrade |  | Retail - Strip Mall Continuous |  | 1926.294 | 1930.137 | 2156.856 | 2174.435 | 2165.03 | 93 | CZ+Fu*(1.077*Tc-10.697*Th+6.91*Ws-1117.18)+Tc*(0.0583*Ws-7.54)+1.231*Ws | 4370.167 | 4243.658
Category | Input | Retail - Strip Mall Intermittent |  | 656.479 | 673.257 | 835.906 | 850.322 | 869.921 |  | CZ+0.0894*Fu*Tc+Th*(-0.0142*Tc+0.04*Ws-5.278)+0.884*Ws | 5088.212 | 5057.1164
Tons Cooling Capacity | 10 | [9 empty] | Baseline | Upgrade
kBtuh Heating Capacity | 230 | Natural Gas Energy Use Climate Zone Coefficients and Minimum Weekly Hours Occupied | [7 empty] | EQUATIONS (NATURAL GAS) | Therms/kbtuh | Therms/kbtuh
Building Type | Office - Low Rise | Building Type and Fan Mode During Occupied Period |  | Climate Zone Coefficient (CZ) |  |  |  |  | Minimum Ws
Fan Mode During Occupied Periods | Continuous |  |  | 1 | 2 | 3 | 4 | 5
Fan Mode During Unoccupied Periods | Intermittent | Assembly Continuous |  | 19.872 | 17.83 | 15.828 | 15.282 | 13.482 | 98 | CZ+Fu*(0.232*Th+0.0984*Ws-18.79)+Th*(0.00271*Ws-0.535)+0.0142*Ws | 5026.995 | 5025.4555
Energy Type | Electric Energy | Assembly Intermittent |  | 0.237 | 0.0989 | 0.0267 | -0.0131 | -0.0871 |  | CZ+Fu*(0.00405*Th+0.000519*Ws-0.11)+Th*(0.0000689*Ws-0.0118)+0.0022*Ws | 5039.6315 | 5039.5919
Climate Zone | 2 | Convenience Store Continuous |  | 1.493 | 1.081 | 0.782 | 0.544 | 0.114 | 108 | CZ+Fu*(0.00545*Th-0.00251*Ws+0.416)+Th*(0.000123*Ws-0.0204)+0.00183*Ws | 5039.9706 | 5039.8888
Degrees of Cooling Setback | 6 | Convenience Store Intermittent |  | 1.128 | 0.854 | 0.619 | 0.437 | 0.0854 |  | CZ+Fu*(0.00231*Th-0.0349)+Th*(0.000309*Ws-0.0494)+0.00266*Ws | 5039.7034 | 5039.4024
Degrees of Heating Setback | 10 | Office - Low Rise Continuous |  | 1.718 | 1.317 | 0.971 | 0.739 | 0.319 | 55 | CZ+Fu*(0.0205*Th+0.364)+Th*(0.00046*Ws-0.0554)+0.00169*Ws | 5040.0489 | 5039.9529
|  | Office - Low Rise Intermittent |  | 3.447 | 3.022 | 2.503 | 2.251 | 1.646 |  | CZ+Fu*(0.00745*Th-0.142)+Th*(0.00077*Ws-0.111)+0.00199*Ws | 5039.5594 | 5038.9474
Calculation Parameters |  | Religious Facility Continuous |  | 6.294 | 5.55 | 4.678 | 4.202 | 3.122 | 133 | CZ+0.00791*Fu*Th+Th*(0.00096*Ws-0.167)+0.00184*Ws | 5039.6932 | 5038.6303
Climate Zone Coefficient | 5039.592 | Religious Facility Intermittent |  | 5.914 | 5.368 | 4.557 | 4.137 | 3.246 |  | CZ+Fu*(0.00143*Th-0.0309)+Th*(0.0008*Ws-0.134)+0.00219*Ws | 5039.6816 | 5038.7959
Weekly Hours | 55 | Restaurant - Fast Food Continuous |  | 8.383 | 7.211 | 6.034 | 5.767 | 4.71 | 108 | CZ+Fu*(0.0431*Th+0.0424*Ws-7.517)+Th*(0.00113*Ws-0.213)+0.0119*Ws | 5035.0615 | 5033.984
|  | Restaurant - Fast Food Intermittent |  | 1.227 | 0.636 | 0.302 | 0.102 | -0.262 |  | CZ+Fu*(0.0125*Th+0.0036*Ws-0.71)+Th*(0.000329*Ws-0.0615)+0.00738*Ws | 5039.4859 | 5039.1768
Upgrade |  | Restaurant - Full Service Continuous |  | 5.247 | 4.484 | 3.753 | 3.465 | 2.627 | 117 | CZ+Fu*(0.00445*Ws-0.535)+Th*(0.000679*Ws-0.1)+0.00218*Ws | 5039.4216 | 5038.7951
kWH | 22699.9 | Restaurant - Full Service Intermittent |  | 0.951 | 0.704 | 0.51 | 0.381 | 0.0746 |  | CZ+Fu*(0.00144*Th+0.000262*Ws-0.0553)+Th*(0.00018*Ws-0.0299)+0.00166*Ws | 5039.6424 | 5039.4568
|  | Retail - Department Store Continuous |  | 4.385 | 3.854 | 3.192 | 2.784 | 1.858 | 93 | CZ+0.00203*Fu*Th+Th*(0.000591*Ws-0.0812)+0.00194*Ws | 5039.6987 | 5039.232
|  | Retail - Department Store Intermittent |  | 3.061 | 2.672 | 2.182 | 1.829 | 1.008 |  | CZ+Th*(0.000406*Ws-0.0611)+0.00228*Ws | 5039.7174 | 5039.3297
Energy Savings |  | Retail - Strip Mall Continuous |  | 3.917 | 3.394 | 2.728 | 2.364 | 1.617 | 93 | CZ+Fu*(0.00998*Th+0.00207*Ws-0.206)+Th*(0.000665*Ws-0.101)+0.00292*Ws | 5039.6604 | 5039.116
kWH | 5114.22 | Retail - Strip Mall Intermittent |  | 2.659 | 2.292 | 1.811 | 1.543 | 0.909 |  | CZ+Fu*(0.00383*Th-0.0656)+Th*(0.000575*Ws-0.0912)+0.00249*Ws | 5039.6633 | 5039.1059
% Savings | 18.39%
|  | Building Type & Fan Mode | Office - Low Rise Continuous |  |  |  | Assembly Continuous
|  | Modes | Continuous | Intermittent
|  | Building Type | Ws
|  | Assembly | 98
|  | Convenience Store | 108
|  | Office - Low Rise | 55
|  | Religious Facility | 133
|  | Restaurant - Fast Food | 108
|  | Restaurant - Full Service | 117
|  | Retail - Department Store | 93
|  | Retail - Strip Mall | 93
|  | Upgrade: | Office - Low Rise Continuous
Electric Energy
Natural Gas Energy

## Install KE2 Therm Controllers (hidden)
Install KE2 Therm Controllers
Source | IL TRM 4.6.6 Page 646
IL Link | https://ilsag.s3.amazonaws.com/IL-TRM_Effective_010122_v10.0_Vol_2_C_and_I_09242021.pdf
Instructions
Please populate the fields in orange with the appropriate data.
Category | Input | Savings Per Motor
Evaporator Fan Motor Rating (ECM) | 3/4 HP | Evaporator Fan Motor Rating (ECM) | Annual kWh Savings per Motor | Peak kW Savings per Motor
Number of Motors | 1 | 16 W | 198 | 0.023
|  | 1/15 - 1/20 HP | 293 | 0.033
ΔkWH | 3209 | 1/5 HP | 856 | 0.098
ΔkW | 0.4 | 1/3 HP | 1419 | 0.162
ΔTherms | 0 | 1/2 HP | 2126 | 0.243
|  | 3/4 HP | 3209 | 0.366

## Evaporator Defrost Control (hidden)
Evaporator Defrost Control
Source | EV TRM Page 170
Link | https://puc.vermont.gov/sites/psbnew/files/doc_library/ev-technical-reference-manual.pdf
Instructions
Please populate the fields in orange with the appropriate data.
Select 'Yes' if a suction temperature of < -20F is applicable. Otherwise 'No'
Category | Input | kW of Defrost Element per Evaporator Fan | % Defrost Cycles Saved | Bonus Factor for Reduced Cooling Load |  | Defrost Cycles per Day | Defrost Cycle Duration
Number of Evaporator Fans | 1 | 0.9 | 30% | Suction Temp ≤ -20F | 1.5 | 4 | 20
Defrost Cycles per Day | 4 |  |  | Suction Temp > -20F | 1
Defrost Cycle Duration (min) | 20
Suction Temperature ≤ -20F | Yes
ΔkWH | 195
ΔkW | 0.4
ΔTherms | 0
Note: This ECM is not listed on the IL TRM. We have approval to use the TRM from EV

## Revision Tracker (hidden)
Revision History
Version (#.#) | Last Revised | Nexant Engineer's Initials | Changes
v1.1 | 2019-02-13 | RO | Added Programmable T-stat and Q-Sync Motor tab Updated sourcing information